## Assumptions
NEW BALTIMORE PROTO-SCHEDULE & SEQUENCING MODEL — ASSUMPTIONS
v1 · Aug 5, 2026 · CVR Engineering · Blue/yellow = editable inputs; validate with HWC field before any number goes to DTE.
PRODUCTION RATES (industry-typical rural distribution rebuild — REPLACE with HWC actuals)
Poles set + framed per crew-day | 2.5 | Rural OH distribution, incl. hardware/framing
Conductor strung per crew-day (ft) | 4000 | 3-phase pull incl. sagging/clipping, rural spans
Transformers hung + connected per crew-day | 4 | Pole-mount, incl. cutouts/arresters
Cutover / energize days per CWO | 1 | Switching, phasing, load checks — per work order
Restoration as % of construction crew-days | 10% | Cleanup, seeding, matting removal
MOBILIZATION & CREW ECONOMICS
Mob + demob crew-days per mobilization event | 2 | Yard load-out, travel, setup/teardown
Fixed cost per mobilization event ($) | 7500 | Traffic setup, delivery staging, permits admin, equip moves
Ramp-up productivity loss per cold start (crew-days) | 0.8 | First ~2 days at reduced output on unfamiliar site
Fully burdened crew cost per day ($) | 8500 | 4-person crew + foreman share + equipment spread
Field supervision + PM cost per calendar week ($) | 6000 | GF/superintendent + PM attributable to program
SEQUENCING EFFECT
Campaign productivity uplift on construction crew-days | 8% | Crew continuity/learning; industry range 5-15%
Number of campaigns (geographic groupings) | 4 | ASSUMED — replace with real corridor groupings
PROGRAM EXTRAPOLATION
These 15 CWOs as share of total OH program | 95% | REVISED from DTE Maximo workbook: our 15 CWOs cover ~97% of program install wire (141,020 ft total). Was 0.50 placeholder.
CALENDAR
Construction start | 2027-04-05 | First Monday April 2027 — "next spring"
HARDENING CHECKLIST (converts strawman → DTE-grade)
1. Replace production rates with HWC estimate/actuals (per-WO labor breakdown)
2. Replace campaign groupings with real geography/circuit adjacency
3. Add remaining ~16 OH work orders (have 15 of 39; UG deletions TBD)
4. Add TRK-4911 predecessor dates + DTE outage windows + WO release plan
5. Validate mob fixed cost and supervision rate with finance

## Scope & Durations
CWO | Poles | OH Conductor (ft) | Transformers | CUE Material $ | Pole Days | Stringing Days | Xfmr Days | Cutover | Restoration | Construction Crew-Days | Baseline Mob+Demob | Baseline Ramp Loss | Baseline Total Crew-Days
73232522 | 30 | 9776 | 12 | 143455.15 | 12 | 2.444 | 3 | 1 | 1.7444 | 20.1884 | 2 | 0.8 | 22.9884
73234686 | 23 | 8311 | 9 | 114600.29 | 9.2 | 2.0777 | 2.25 | 1 | 1.3528 | 15.8805 | 2 | 0.8 | 18.6805
73239897 | 25 | 5946 | 7 | 113119.61 | 10 | 1.4865 | 1.75 | 1 | 1.3236 | 15.5602 | 2 | 0.8 | 18.3602
73239916 | 33 | 6580 | 13 | 181388.96 | 13.2 | 1.645 | 3.25 | 1 | 1.8095 | 20.9045 | 2 | 0.8 | 23.7045
73239926 | 25 | 6114 | 5 | 107363.49 | 10 | 1.5285 | 1.25 | 1 | 1.2778 | 15.0564 | 2 | 0.8 | 17.8563
73240913 | 36 | 22026 | 9 | 193534.58 | 14.4 | 5.5065 | 2.25 | 1 | 2.2157 | 25.3722 | 2 | 0.8 | 28.1721
73242557 | 20 | 4757 | 4 | 66525.33 | 8 | 1.1892 | 1 | 1 | 1.0189 | 12.2082 | 2 | 0.8 | 15.0082
73242619 | 18 | 8446 | 6 | 65028.72 | 7.2 | 2.1115 | 1.5 | 1 | 1.0812 | 12.8926 | 2 | 0.8 | 15.6927
73244139 | 38 | 8978 | 6 | 102398.73 | 15.2 | 2.2445 | 1.5 | 1 | 1.8944 | 21.839 | 2 | 0.8 | 24.639
73279347 | 0 | 145 | 0 | 25975.2 | 0 | 0.03625 | 0 | 0 | 0.003625 | 0.039875 | 2 | 0.8 | 2.8399
73301547 | 32 | 13450 | 6 | 93529.72 | 12.8 | 3.3625 | 1.5 | 1 | 1.7663 | 20.4288 | 2 | 0.8 | 23.2288
73301585 | 33 | 16885 | 3 | 84563.74 | 13.2 | 4.2213 | 0.75 | 1 | 1.8171 | 20.9884 | 2 | 0.8 | 23.7884
73305080 | 15 | 10960 | 0 | 36177.1 | 6 | 2.74 | 0 | 1 | 0.874 | 10.614 | 2 | 0.8 | 13.414
73358165 | 3 | 668 | 0 | 7005.13 | 1.2 | 0.167 | 0 | 1 | 0.1367 | 2.5037 | 2 | 0.8 | 5.3037
73802595 | 1 | 17247 | 4 | 43971.25 | 0.4 | 4.3117 | 1 | 1 | 0.57117 | 7.2829 | 2 | 0.8 | 10.0829
TOTAL | 332 | 140289 | 84 | 1378637 | 132.8 | 35.0722 | 21 | 14 | 18.8872 | 221.7595 | 30 | 12 | 263.7595

## Scenario Comparison
SEQUENCING SCENARIOS — 15 RECONCILED CWOs
Baseline = each WO standalone as priced. Campaign = corridor-grouped continuous execution. Same scope — the delta is structure.
| BASELINE (as priced) | CAMPAIGN — 2 crews | CAMPAIGN — 3 crews | CAMPAIGN — 4 crews
Mobilization events | 15 | 4 | 4 | 4
Construction crew-days (scope work) | 221.7595 | 204.0187 | 204.0187 | 204.0187
Mob/demob crew-days | 30 | 8 | 8 | 8
Ramp-up loss crew-days | 12 | 3.2 | 3.2 | 3.2
TOTAL crew-days | 263.7595 | 215.2187 | 215.2187 | 215.2187
Crews | 1 | 2 | 3 | 4
Calendar working days | 263.7595 | 107.6094 | 71.7396 | 53.8047
Calendar weeks | 52.7519 | 21.5219 | 14.3479 | 10.7609
Crew labor cost | 2241955.5375 | 1829359.0945 | 1829359.0945 | 1829359.0945
Mobilization fixed cost | 112500 | 30000 | 30000 | 30000
Supervision/PM (calendar-driven) | 316511.37 | 129131.2302 | 86087.4868 | 64565.6151
TOTAL modeled field cost | 2670966.9075 | 1988490.3247 | 1945446.5813 | 1923924.7096
SAVINGS vs baseline — these 15 CWOs |  | 682476.5828 | 725520.3262 | 747042.1979
EXTRAPOLATED program savings (÷ program share) |  | 718396.4029 | 763705.6065 | 786360.2083
READ: cost savings are nearly crew-count-independent (same crew-days); crew count drives the CALENDAR (fit within the spring-to-freeze window).
Not modeled (upside): contingency de-stacking across WOs, bulk material staging, per-WO traffic re-setups, weather-window optimization, rework avoided by EOR-verified procurement.
Not modeled (risk): outage availability, TRK-4911 timing, crew availability, geography making assumed groupings infeasible.
Extrapolation assumes savings scale linearly with program share — refine when the full 39-WO list is loaded.

## Schedule Skeleton (3-crew)
ILLUSTRATIVE CAMPAIGN SEQUENCE — 3 CREWS, START APR 5 2027
Campaign groupings are SIZE-BALANCED PLACEHOLDERS (no geography yet). Dates via WORKDAY() — editing assumptions re-flows dates on recalc.
Campaign | Crew | CWO | Crew-Days (uplifted) | Start | Finish
C1 | Crew 1 | 73240913 | 23.3424 | 2027-04-05 | 2027-05-06
C1 | Crew 1 | 73239897 | 14.3153 | 2027-05-07 | 2027-05-27
C1 | Crew 1 | 73242619 | 11.8612 | 2027-05-28 | 2027-06-15
C2 | Crew 2 | 73244139 | 20.0918 | 2027-04-05 | 2027-05-03
C2 | Crew 2 | 73234686 | 14.6101 | 2027-05-04 | 2027-05-25
C2 | Crew 2 | 73239926 | 13.8518 | 2027-05-26 | 2027-06-15
C2 | Crew 2 | 73358165 | 2.3034 | 2027-06-16 | 2027-06-18
C3 | Crew 3 | 73301585 | 19.3093 | 2027-04-05 | 2027-04-30
C3 | Crew 3 | 73232522 | 18.5733 | 2027-05-03 | 2027-05-28
C3 | Crew 3 | 73242557 | 11.2315 | 2027-05-31 | 2027-06-15
C3 | Crew 3 | 73279347 | 0.036685 | 2027-06-16 | 2027-06-17
C4 | Crew 1 | 73239916 | 19.2321 | 2027-06-16 | 2027-07-13
C4 | Crew 1 | 73301547 | 18.7945 | 2027-07-14 | 2027-08-10
C4 | Crew 1 | 73305080 | 9.7649 | 2027-08-11 | 2027-08-25
C4 | Crew 1 | 73802595 | 6.7003 | 2027-08-26 | 2027-09-06
Per-campaign mob (2 crew-days) applies at campaign boundaries; cutover/restoration included in durations. All open-order material dates (Sept-Nov 2026) clear the Apr 2027 start.
Formulas:
Start = WORKDAY([Finish, row above],1)
Finish = WORKDAY([Start],MAX(ROUND([Crew-Days (uplifted)],0),1))